## Slide 1: Procuring Better Building Performance Keynsham Civic Centre Case Study
Tamsin Tweddell
T.Tweddell@maxfordham.com

## Slide 2
Keynsham civic centre
Notes: Client: Bath & North East Somerset Council
Architect: ARH (Aedas)
Main Contractor: Willmott Dixon
Commissioning Manager: Core Groupmedium
Area: 6300m2 office (+1200m2 library, 1600m2 retail)
Cost: £23M; £2400/m2
Procurement: 2 stage D&B; we stayed client side
Completion: November 2014
Intended occupancy: 455 people

## Slide 3: THE CLIENT’S BRIEF:
Ultimately, the success of the building will be judged on its operational energy use and resultant carbon emissions. Therefore, the current aspiration is that the development should achieve a DEC rating of A by the end of the second full year of operation.

## Slide 4: Procuring Soft Landings
Low energy design – the easy bit!
Develop an Energy Budget
Energy risk management
Embed in contract
Aftercare programme – monitoring & fine tuning
 Lessons learnt
CLOSING THE PERFORMANCE GAP: OUR APPROACH

## Slide 5
ENERGY BUDGET
Unregulated
Regulated
Net CO2
PV
Server (incl cooling)
Notes: Highlights key risks to operational outcomes (energy, comfort, ease of use etc)
Offers mitigation measures for each stage of the project.
Can be informed by lessons learnt from previous projects, reality checking exercises, usability workshops.

## Slide 6: ENERGY RISK MANAGEMENT

## Slide 7
LIGHTING
RISK
INADEQUATE CONTROLS INSTALLATION AND/OR COMMISSIONING
USERS DON’T UNDERSTAND CONTROLS OR FIND INCONVENIENT
MITIGATION
SIMPLIFY CONTROL STRATEGY
ENGAGE WITH USERS DURING DESIGN
USE OUTSIDE CORE HOURS NOT ALLOWED FOR, EG FOR CLEANERS
CALCS TO CONSIDER OUT-OF-HOURS USE
MONITOR COMMISSIONING
REVIEW PERFORMANCE POST OCCUPANCY AND FINE-TUNE

## Slide 8
REFINE THE ENERGY BUDGET
CIBSE TM 54
Agree operating conditions which achieve the energy budget
= Energy Baseline
Understand that reality will be different!

## Slide 9
EMBEDDING THE ENERGY BUDGET IN THE CONTRACT
Energy use category
Annual energy budget
Within contractor’s control
Outside contractor’s control
Assumptions:
Lighting
Lux levels
Power density
Controls as specified
Task lights
Hours of operation
External illuminance
31,000 kWh
16,000 kgCO2

## Slide 10
AFTERCARE: MONITORING & VERIFICATION
Monitor
Review
Identify
Adjust
Notes: Monitor, review, identify, adjust

## Slide 13
Year 1
Year 1+9mth
58% reduction, year 1 to 1+9mth

## Slide 14
Year 1
Year 1 + 9mths
Notes: Regulated is 125% over budget
Unregulated only 4% over budget
Commissioning still an issue.

## Slide 15
COULD DO BETTER
Passive robust design
Energy Budget/Contract
Limited VE
Contractor is still there !?
Commissioning Manager
Stakeholder (FM) engagement
Delivered within local authority budget
Client is very proud of the building
M&E contractor
Lighting controls
BMS – still not working
Energy metering – still read manually
WORKED WELL

## Slide 16: Procuring Soft Landings
The value of the independent commissioning manager
The importance of getting the right M&E contractor
Consultants are nervous about ‘predicting’ operational energy use
LESSONS FOR FUTURE PROJECTS
Notes: The value of the independent commissioning manager
The importance of getting the right M&E contractor
  Tender must enable evaluation on quality, not just price. Clear quality criteria must be set.
  M&E must be priced on design, not an allowance

## Slide 17: THANK YOU
Tamsin Tweddell
Procuring Better Building Performance
17th May 2017